## Facility
ASHRAE Level II energy audit data template
Facility data, utility analysis, end-use inventory and ECM economics
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Facility
Facility name |  |  | Client site
Address / GPS
Building type | Manufacturing |  | Manufacturing / Office / Hotel / Hospital
Gross floor area | 4500 | m² | Conditioned + unconditioned
Conditioned floor area | 3100 | m²
Year built / last major retrofit | 2012
Operating hours per week | 120 | h | Include shifts and weekends
Occupants (peak) | 180 | no.
Audit
Audit level | ASHRAE Level II |  | Energy survey and engineering analysis
Audit date
Lead auditor | Bethwel Kimaru
Baseline period | 12 months |  | Use 12 consecutive months of bills
Electricity tariff | 0.19 | USD/kWh | Blended energy + demand
Demand charge | 12 | USD/kVA/month | From the utility bill
Fuel tariff (diesel/LPG) | 1.15 | USD/litre
Grid emission factor | 0.28 | kgCO₂e/kWh | National grid factor

## Utility data
Utility bill analysis
Twelve consecutive months from the meter or utility statements
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Month | Electricity (kWh) | Peak demand (kVA) | Load factor | Fuel (litres) | Electricity cost | Fuel cost | Total cost
Jan | 0 | 0 | 0% | 0 | 0 | 0 | 0
Feb | 0 | 0 | 0% | 0 | 0 | 0 | 0
Mar | 0 | 0 | 0% | 0 | 0 | 0 | 0
Apr | 0 | 0 | 0% | 0 | 0 | 0 | 0
May | 0 | 0 | 0% | 0 | 0 | 0 | 0
Jun | 0 | 0 | 0% | 0 | 0 | 0 | 0
Jul | 0 | 0 | 0% | 0 | 0 | 0 | 0
Aug | 0 | 0 | 0% | 0 | 0 | 0 | 0
Sep | 0 | 0 | 0% | 0 | 0 | 0 | 0
Oct | 0 | 0 | 0% | 0 | 0 | 0 | 0
Nov | 0 | 0 | 0% | 0 | 0 | 0 | 0
Dec | 0 | 0 | 0% | 0 | 0 | 0 | 0
Total | 0 | 0 |  | 0 | 0 | 0 | 0
Energy use intensity (kWh/m²/yr) | #VALUE!
Annual emissions (tCO₂e) | 0

## End use inventory
End-use inventory
Measured or nameplate loads with operating hours — the basis of the energy balance
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
System / equipment | Qty | Rated kW each | Load factor | Hours/year | Annual kWh | % of total kWh | Annual cost
Compressed air | 2 | 45 | 0.65 | 6000 | 351000 | 24.61% | 66690
Process motors & drives | 24 | 7.5 | 0.55 | 5500 | 544500 | 38.18% | 103455
Chillers / cold rooms | 2 | 30 | 0.6 | 6500 | 234000 | 16.41% | 44460
HVAC air handling | 6 | 5.5 | 0.7 | 4500 | 103950 | 7.288% | 19750.5
Lighting — interior | 1 | 22 | 0.9 | 4200 | 83160 | 5.831% | 15800.4
Lighting — exterior | 1 | 6 | 1 | 4380 | 26280 | 1.843% | 4993.2
Boiler / steam auxiliaries | 1 | 15 | 0.5 | 3500 | 26250 | 1.84% | 4987.5
Water pumping | 3 | 5.5 | 0.5 | 3000 | 24750 | 1.735% | 4702.5
IT, office & small power | 1 | 18 | 0.6 | 3000 | 32400 | 2.272% | 6156
Other / unaccounted | 1 | 0 | 0 | 0 | 0 | 0% | 0
Total |  |  |  |  | 1426290 | 100% | 270995.1

## ECM measures
Energy conservation measures
Level II requires savings, cost and simple payback for each recommended measure
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Measure | kWh saved/yr | kW demand saved | Fuel saved (l/yr) | Annual saving | Capex | Payback (yr) | tCO₂e avoided
LED retrofit + occupancy sensors | 38000 | 8 | 0 | 8372 | 12000 | 1.4333 | 10.64
Compressed air leak survey & repair | 42000 | 6 | 0 | 8844 | 4500 | 0.50882 | 11.76
VSDs on pumps and fans | 55000 | 10 | 0 | 11890 | 18000 | 1.5139 | 15.4
Power factor correction to 0.97 | 0 | 45 | 0 | 6480 | 9000 | 1.3889 | 0
Chiller setpoint & sequencing optimisation | 26000 | 5 | 0 | 5660 | 3000 | 0.53004 | 7.28
Boiler tune-up & insulation | 0 | 0 | 9000 | 10350 | 7000 | 0.67633 | 0
Rooftop solar PV (see PV calculator) | 180000 | 30 | 0 | 38520 | 140000 | 3.6345 | 50.4
Sub-metering & energy monitoring | 15000 | 0 | 0 | 2850 | 12000 | 4.2105 | 4.2
Portfolio total | 356000 |  |  | 92966 | 205500 | 2.2105 | 99.68
Savings as % of baseline spend | 0%

## Notes & method
Method notes
How to use this template
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
1. Complete the Facility sheet first — tariffs and floor area drive every other calculation.
2. Enter 12 consecutive months on Utility data, straight from the bills or the revenue meter. Do not annualise a partial year.
3. Build the End-use inventory from nameplate data corrected by spot measurements (clamp meter, power logger, run-hour meters).
4. Reconcile: the end-use total should land within ±10 % of metered annual kWh. Put the difference in 'Other / unaccounted' and explain it.
5. Quantify each ECM with an engineering calculation, not a rule of thumb. State assumptions next to each measure.
6. ASHRAE Level II also requires a breakdown of capital vs O&M measures and an assessment of the measures needing a Level III analysis.
7. Report savings and demand reduction separately — many tariffs pay more for kVA than for kWh.
8. Blue cells are inputs, black cells are formulas, yellow highlights key assumptions to confirm with the client.