## Inputs
Solar PV sizing calculator
Off-grid, hybrid and grid-tied sizing from a daily load profile
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Site & resource
Site name | Nairobi plant |  | Free text
Latitude | -1.29 | ° | Negative = southern hemisphere
Peak sun hours (PSH) | 5.4 | kWh/m²/day | Design month average — use the worst month
Ambient design temperature | 32 | °C | Used for temperature derate
System configuration
System type | Hybrid |  | Off-grid / Hybrid / Grid-tied
System DC voltage | 48 | V | 12 / 24 / 48 V for battery systems
Days of autonomy | 1 | days | 0 for grid-tied, 1–3 for off-grid
Battery depth of discharge | 0.8 | fraction | 0.8 lithium, 0.5 lead-acid
Battery round-trip efficiency | 0.94 | fraction | 0.94 LFP, 0.80 lead-acid
Inverter efficiency | 0.96 | fraction | From datasheet at typical load
Losses
Soiling loss | 0.03 | fraction | 0.02–0.06, higher near dust/industry
Temperature loss | 0.08 | fraction | ≈0.4 %/°C above 25 °C cell temp
Wiring & mismatch loss | 0.03 | fraction | Keep DC volt drop under 2 %
Inverter & MPPT loss | 0.04 | fraction | 1 - inverter efficiency, plus MPPT
Module & equipment
Module rated power | 550 | Wp | STC nameplate
Module Voc at STC | 49.8 | V | For string voltage check
Module Vmp at STC | 41.8 | V
Voc temperature coefficient | -0.0027 | /°C | Typically -0.0025 to -0.003
Inverter max DC input voltage | 500 | V | From datasheet
Cost per Wp installed | 0.85 | USD/Wp | Turnkey, for the summary
Grid tariff | 0.19 | USD/kWh | Blended, for payback

## Load profile
Daily load profile
List every load; the calculator sizes from the daily energy total
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Load | Qty | Watts each | Hours/day | Duty factor | Daily energy (Wh) | AC or DC
LED lighting | 40 | 18 | 12 | 1 | 8640 | AC
Office workstations | 12 | 120 | 9 | 0.8 | 10368 | AC
Borehole pump | 1 | 1500 | 3 | 1 | 4500 | AC
Cold room compressor | 1 | 2200 | 10 | 0.6 | 13200 | AC
Workshop tools | 1 | 3000 | 4 | 0.35 | 4200 | AC
Control panel / PLC & instruments | 1 | 250 | 24 | 1 | 6000 | DC
Security & CCTV | 1 | 180 | 24 | 1 | 4320 | DC
Spare / future load | 1 | 0 | 0 | 1 | 0 | AC
Total daily energy |  |  |  |  | 51228
Peak simultaneous demand (W) |  |  |  |  | 6172

## Sizing
Sizing results
All values calculated — change the Inputs and Load profile sheets only
Bethwel Kimaru · bethwelkimaru.space · blue = your input, black = calculated
Result | Value | Unit | Basis
Daily energy demand | 51.228 | kWh/day | Sum of the load profile
Peak demand | 6.172 | kW | Simultaneous load estimate
Total derate factor | 0.831 | fraction | Product of the four loss inputs
Required array energy | 61.646 | kWh/day | Demand corrected for system losses
Array size required | 11.4159 | kWp | Array energy ÷ peak sun hours
Modules required | 21 | no. | Rounded up to whole modules
Installed array capacity | 11.55 | kWp | Modules × module rating
Expected annual yield | 18917.8221 | kWh/year | Derated, design-month PSH (conservative)
Battery energy required | 70.9608 | kWh | Autonomy ÷ DoD ÷ efficiencies
Battery bank capacity | 1478.3494 | Ah | At the system DC voltage
Inverter continuous rating | 7.715 | kW | Peak demand + 25 % headroom
Max modules per string | 9 | no. | Voc at −10 °C vs inverter max input
Suggested string count | 3 | no. | Modules ÷ max per string
Indicative capex | 9817.5 | USD | Installed cost per Wp × array size
Annual energy value | 3594.3862 | USD/year | Yield × tariff
Simple payback | 2.7313 | years | Capex ÷ annual value
Check: string Voc at −10 °C must stay below the inverter maximum. Verify cable volt drop < 2 % DC and < 1 % AC.